## Graphs
Churn No | Time | Temperature
|  | CCW In | CCW Out | ∆T | Churn
| 11:20 | 32 | 31.8 | -0.2 | 27.5
7 | 11:25 | 31.8 | 31.4 | -0.4 | 31
| 11:30 | 32 | 31.4 | -0.6 | 30
| 11:35 | 31.6 | 31.6 | 0 | 31.8
| 11:40 | 31.4 | 31.6 | 0.2 | 32.5
| 11:45 | 31.4 | 32 | 0.6 | 34
| 11:50 | 31.6 | 31.8 | 0.2 | 34.9
| 11:55 | 31.8 | 32 | 0.2 | 35.2
| 12:00 | 31.6 | 32.2 | 0.6 | 36.1
| 12:05 | 31.4 | 31.8 | 0.4 | 38.5
| 12:10 | 31.6 | 31.8 | 0.2 | 38.5
| 12:15 | 31.6 | 31.8 | 0.2 | 39.2
| 12:20 | 31.8 | 32.2 | 0.4 | 40
| 12:25 | 31.6 | 32 | 0.4 | 40
| 12:30 | 31.6 | 32 | 0.4 | 40.3
| 12:35 | 31.6 | 32.2 | 0.6 | 40.6
| 12:40 | 31.6 | 32.2 | 0.6 | 40.6
| 12:45 | 31.4 | 32 | 0.6 | 40.6
| 12:50 | 31.4 | 32.2 | 0.8 | 40.8
| 12:55 | 31.5 | 31.8 | 0.3 | 41
|  |  | Average: | 0.275 | 36.655
Churn No | Time | Temperature
|  | CCW In | CCW Out | ∆T | Churn
| 12:45 | 31.6 | 31.2 | -0.4 | 27.5
8 | 12:50 | 31.4 | 31.2 | -0.2 | 28.1
| 12:55 | 31.4 | 31.2 | -0.2 | 29.5
| 13:00 | 31.6 | 31.2 | -0.4 | 30
| 13:05 | 31.4 | 31.4 | 0 | 31
| 13:10 | 31.5 | 31.4 | -0.1 | 32.1
| 13:15 | 31.6 | 31.8 | 0.2 | 33.2
| 13:20 | 31.6 | 31.8 | 0.2 | 34
| 13:25 | 31.6 | 32 | 0.4 | 35.5
| 13:30 | 31.4 | 31.8 | 0.4 | 37.5
| 13:35 | 31.6 | 32 | 0.4 | 38.5
| 13:40 | 31.6 | 31.8 | 0.2 | 39
| 13:55 | 31.4 | 31.6 | 0.2 | 40
| 14:00 | 31.4 | 31.6 | 0.2 | 40
| 14:05 | 31.6 | 32 | 0.4 | 40.5
| 14:10 | 31.4 | 31.8 | 0.4 | 41
| 14:15 | 31.4 | 31.8 | 0.4 | 41
| 14:20 | 31.4 | 31.8 | 0.4 | 41
| 14:25 | 31.6 | 32 | 0.4 | 41.1
| 14:30 | 31.4 | 32 | 0.6 | 41
|  |  | Average: | 0.175 | 36.075
Churn No | Time | Temperature
|  | CCW In | CCW Out | ∆T | Churn
| 13:25 | 31.5 | 31.6 | 0.1 | 29.3
4 | 13:30 | 31.4 | 31.5 | 0.1 | 28.2
| 13:35 | 31.4 | 31.4 | 0 | 27.5
| 13:40 | 31.6 | 31.6 | 0 | 27.1
| 13:55 | 31.4 | 31.2 | -0.2 | 28.5
| 14:00 | 31.4 | 31.4 | 0 | 29.7
| 14:05 | 31.4 | 31.4 | 0 | 30.6
| 14:10 | 31.4 | 31.4 | 0 | 31.7
| 14:15 | 31.4 | 31.6 | 0.2 | 32.8
| 14:20 | 31.4 | 31.6 | 0.2 | 33.6
| 14:25 | 31.4 | 31.8 | 0.4 | 34.5
| 14:30 | 31.2 | 31.6 | 0.4 | 35.7
| 14:35 | 31.2 | 31.6 | 0.4 | 36.9
| 14:40 | 31.2 | 31.6 | 0.4 | 37.7
| 14:45 | 31.4 | 31.8 | 0.4 | 38.3
| 14:50 | 31.6 | 31.8 | 0.2 | 38.7
| 14:55 | 31.4 | 31.8 | 0.4 | 38.9
| 15:00 | 31.4 | 31.8 | 0.4 | 39
| 15:05 | 31.4 | 31.8 | 0.4 | 39.1
| 15:10 | 31.6 | 32.2 | 0.6 | 39.1
| 15:15 | 31.6 | 32.2 | 0.6 | 39.2
| 15:20 | 31.6 | 32.2 | 0.6 | 39.2
| 15:25 | 31.4 | 31.8 | 0.4 | 39.2
| 15:30 | 31.4 | 31.8 | 0.4 | 39.3
| 15:35 | 31.4 | 32.2 | 0.8 | 39.2
|  |  | Average: | 0.36 | 36.62
Churn No | Time | Temperature
|  | CCW In | CCW Out | ∆T | Churn
| 14:20 | 31.4 | 31.2 | -0.2 | 26.5
1 | 14:25 | 31.6 | 31.4 | -0.2 | 27.5
| 14:30 | 31.6 | 31.4 | -0.2 | 28.65
| 14:35 | 31.4 | 31.2 | -0.2 | 29.3
| 14:40 | 31.6 | 31.4 | -0.2 | 30.4
| 14:45 | 31.6 | 31.4 | -0.2 | 31.2
| 14:50 | 31.6 | 31.6 | 0 | 32.5
| 14:55 | 31.4 | 31.6 | 0.2 | 33.3
| 15:00 | 31.4 | 31.6 | 0.2 | 34.3
| 15:05 | 31.6 | 31.6 | 0 | 35.1
| 15:10 | 31.8 | 32.1 | 0.3 | 36.1
| 15:15 | 31.8 | 32 | 0.2 | 37.44
| 15:20 | 31.6 | 32 | 0.4 | 38.7
| 15:25 | 31.4 | 32 | 0.6 | 39.4
| 15:30 | 31.6 | 31.8 | 0.2 | 39.7
| 15:35 | 31.8 | 32.2 | 0.4 | 40
| 15:40 | 31.8 | 32.4 | 0.6 | 40.2
| 15:45 | 31.6 | 32.2 | 0.6 | 40.3
| 15:50 | 31.6 | 32.2 | 0.6 | 40.4
| 15:55 | 31.8 | 32.2 | 0.4 | 40.4
| 16:00 | 32 | 32.4 | 0.4 | 40.4
| 16:05 | 31.6 | 32.2 | 0.6 | 40.5
| 16:10 | 32 | 32.6 | 0.6 | 40.5
| 16:15 | 32 | 32.4 | 0.4 | 40.5
| 16:20 | 32.8 | 33.2 | 0.4 | 40.4
|  |  | Average: | 0.345 | 38.067

## Calculations
Churn Heat Transfer Calculations
DATA
Water flow rate calculations
Pump Capacity | 60 | m3/hr | Volumetric flow rate in header | 0.016667 | m3/s
Header piping diameter(4") | 0.1016 | m | Header piping area | 0.0081073 | m2
Tapping piping diameter(2") | 0.0508 | m | Tapping piping area | 0.0020268 | m2
No of splits | 7 |  | Volumetric flow rate in tapping | 0.002381 | m3/s
Velocity of water in tapping vi | 4.7012 | m/s | Velocity of water in header | 2.0558 | m/s
Properties of water
Dynamic Viscosity µ | 0.000764 | Pa.s | Density ρ | 995 | kg/m3
Thermal Conductivity K | 0.061842 | W/m°C | Specific heat Cp | 4.178 | kJ/kg.K
Prandtl No Pr | 5.2 |  | Specific Volume ν | 1.005 | m3/kg
Expansion Coefficient β | 0.000321 | K-1 | Heat of Vaporization Hν | 2426 | kJ/kg
Properties of CS2
Dynamic Viscosity µ | 0.000421 | Pa.s | Density ρ | 1256 | kg/m3
Thermal Conductivity K | 1.5662 | W/m°C | Specific heat Cp | 1.039 | kJ/kg.K
Prandtl No Pr | 0.865 |  | Specific Volume ν |  | m3/kg
Expansion Coefficient β | 0.2264 | K-1 | Heat of Vaporization Hν |  | kJ/kg
Properties of Mild Steel
Thermal Conductivity K | 31.5 | W/m°C | Density ρ | 7850 | kg/m3
Churn characteristics
Vessel diameter DT | 1.28 | m | Vessel area Ai | 14.6373 | m2
Jacket diameter Dj | 1.4 | m | Jacketed vessel area Ao | 16.2719 | m2
Length L | 3 | m
JACKET SIDE CALCULATION
de | 0.09792 | m | K | 0.61842 | W/m°C
g | 9.81 | m/s2 | Pr | 5.2
µ | 0.000764 | Pa.s
β | 0.000321 | K-1
ρ | 995 | kg/m3
vi | 4.7012 | m/s | sqrt(vi*vA) | 0.21051 | m/s
vA | 0.0094264 | m/s | Re | 26846.0489
Nu | 107.5317 |  | hi=Nu*K/de | 679.1234 | W/m2°C
VESSEL SIDE CALCULATION
Pr | 0.865 |  | K | 1.5662 | W/m°C
g | 9.81 | m/s2 | ∆T | 13.5 | K
µ | 0.000421 | Pa.s | ν | 3.3519e-07
β | 0.2264 | K-1 | DT | 1.28 | m
ρ | 1256 | kg/m3
GrD | 559659905064.019 |  | NuD | 392.0423
ho=Nu*K/DT | 479.7097 | W/m2°C
VESSEL THERMAL RESISTANCE
R | 0.00015092 | W/m°C
OVERALL HEAT TRANSFER COEFFICIENT CALCULATION
hi | 679.1234 |  | ho | 392.0423
1/hi | 0.0014725 |  | 1/ho | 0.0025507
Ai/Ao | 0.89955 |  | Ai/Ao*1/ho | 0.0022945
1/Ui | 0.0059761
Ui | 27.8164
CHURN AVAILABLE AREA CALCULATION
Assumption: We are maintaining constant average churn temperature | [5 empty] | Water flow rate | 2.3691 | kg/s
CHURN #1 | [5 empty] | Heat gained by water | 2720.2202 | W
∆Tm | 4.0284 | K | Availablle churn area | 24.2754 | m2
CHURN #4 | [5 empty] | Water flow rate | 2.3691 | kg/s
∆Tm | 3.7735 | K | Availablle churn area | 27.1705 | m2 | Heat gained by water | 2851.9572 | W
CHURN #7 | [5 empty] | Water flow rate | 2.3691 | kg/s
∆Tm | 4.4111 | K | Availablle churn area | 22.194 | m2 | Heat gained by water | 2723.22 | W
CHURN #8 | [5 empty] | Water flow rate | 2.3691 | kg/s
∆Tm | 3.9868 | K | Availablle churn area | 15.6265 | m2 | Heat gained by water | 1732.9601 | W
NuD = 0.47(GrDPr)1/4
GrD= gβD3∆T/ν2
R=ln(DT/Dj)/2πKL
Since the area available for churn #7 and #8 is less compared to churns #1 and #4, the temperature of the xanthate exiting from them is greater.
Proper flushing of the jackets can be done to avoid this problem.